## Slide 1: Membrane Filtration
Notes: $14,800,000
https://www.kpaengineers.com/portfolio-items/membrane-filtration-plant/
15 MGD
No pretreatment
$22500 /(L/s)
Actuually operates at 11.6 MGD
Project Description: The City of Temple, Texas owns and operates the 11.6 MGD Membrane Water Treatment Plant. The plant was placed into operation in 2004 and operated as originally designed for the first 12 to 15 months. However, over the past several years the plant has not been able to consistently operate at the design capacity. $590,524 to upgrade the chemical cleaning
Realized they needed pretreatment in 2008
Backwash Sedimentation $2,607,785

## Slide 2: Conventional Units in Env. Eng.
Surface loading rates
Flux
gpm/ft2
Lph/m2
A modest proposal.
  Let’s consistently use the simplest SI units so that we can compare across processes and bring physical insight
  The standard unit of time is seconds.

## Slide 3: Membrane Filtration for Drinking Water Treatment
Removal by size exclusion
Size of contaminants
Head loss through a pore
Number of pores per area of membrane
Typical filtration approach velocities
How do they achieve reasonable flow rates per unit area?
Low pressure and high pressure systems
Fouling
DOM removal
Notes: Brent Alspach
Membrane filtration is certainly carving out a substantive niche in drinking water treatment, but I wouldn’t say that they’re generally preferred; nor would I expect them to overtake the use of conventional treatment any time soon.
I’m not aware of any generalized comparison between media (rapid sand) filters and MF/UF, primarily due lots of variability with site-specific factors, the membrane product used, and system capacity, among others. The performance comparison should be pretty straightforward, but the relative costs and other issues (e.g., maintenance, automation, etc.) can be very different from site-to-site and client-to-client.
It might be better to simply stick to performance-based factors in teaching your class, and then noting the other items that are more subjective and can influence the selection of one technology over another. This would have more practical value for your students then some kind of a generalized comparison that is assumed (almost certainly erroneously) to be broadly applicable.
Membranes (and other advanced treatment technologies) are the same as more conventional processes, in which you’d do some calculations to size the system, based on theory described in texts. In practice, as an engineer, you really have to understand what the technology is capable of doing, along with its pros and cons, operational nuances, potential challenges, etc., and then if the technology is a good candidate for an application, you’d rely on the vendor to size the system. Alternatively, if possible within budget and scheduling constraints, you might also conduct a pilot test, which would give the engineer more direct information to specify design criteria. (Just to clarify – this is MF/UF; the paradigm is a bit different than NF/RO.)
There are some AWWA Manuals of Practice for both MF/UF and NF/RO, and those have some interesting information that might be of use. Those are all prepared by volunteers (i.e., people like us who donate our time and expertise) in the profession, so they tend to be more practical than theoretical.

## Slide 4: Pore sizes
Microfiltration
0.1 mm pores
Ultrafiltration
0.01 mm pores
Nanofiltration
0.001 mm pores
Reverse osmosis
Nonporous
Water
Monovalent species (Na+, Cl-)
Dissolved organic matter
Divalent ions (Ca2+, Mg2+)
Small colloids
Viruses
Particles, Sediment
Algae, Protozoa, Bacteria
Membrane filtration
Reverse Osmosis
Notes: MWH's Water Treatment: Principles and Design, Third Edition
Chapter 12 - Membrane Filtration
John Wiley & Sons © 2012

## Slide 5
Parameter | Membrane Filtration | Reverse Osmosis | Rapid Granular Filtration
Mechanism | Straining (size exclusion) | Differences in solubility or diffusivity | Flow constrictions
Removal efficiency | pC* of 6 (99.9999%) | 50% to 99% | ????
Transmembrane pressure | 0.2 - 1 bar | 5 – 85 bar | 
Transmembrane head loss | 2 – 10 m | 50 – 850 m | 2-3 m (0.2 – 0.8 m for StaRS)
Membrane velocity* | 8 – 50 mm/s | 0.3 – 14 mm/s | 1.4 – 4.2 mm/s
Competing process | Floc/floc blanket/sed/filter | Carbon adsorption, ion exchange, precipitative softening, distillation | 
Filter run time | 30 – 90 minutes |  | 1 – 4 days
Backwash duration | 1 – 3 minutes |  | 10-15 minutes
*not pore velocity
Notes: Adapted from Crittenden, John C., and et al.. MWH's Water Treatment: Principles and Design, Third Edition. John Wiley & Sons. © 2012.Skillsoft. <https://proxy.library.cornell.edu/sso/skillport?context=46187> (Accessed April 02, 2019)

## Slide 6: Why membranes?
1993 Milwaukee Cryptosporidiosis outbreak revealed that sand filters can fail
Absolute (almost) barrier to protozoa and bacteria pathogens
Doesn’t require getting the chemical dose right
Simpler to understand how it works
But at the cost of higher energy and more plastic waste)

## Slide 7: Definition of rejection for Membrane and Ultra Filtration
UF membrane retention rating
MF membrane retention rating

## Slide 8: Proposed particle capture mechanisms
Particles strained at the surface
(presumed dominant mechanism)
Colloidal matter adsorbed to wall of pores
Smaller particles trapped by previously strained particles
Notes: http://www.atl.semtechsolutions.com/node/18/membrane-filtration-technology

## Slide 9: Membrane Hydraulics
Head loss through a clean membrane increases linearly with flow rate
Therefore minor losses must be insignificant!
Pores must be relatively long so that entrance and exit losses are insignificant

## Slide 10: Head loss through membranes
Given that the pore diameter and length are poorly defined, a resistance coefficient is used
From Hagen Poiseuille
Comparing the two equations we see that

## Slide 11: Head loss through membranes
100 nm pore diameter
Porosity of 0.15 (I can’t find any data!)
Pore length of 1000 x diameter (0.1 mm)
Approach velocity of 8 mm/s
Temperature of 15 C
Gives a head loss of 2 m

## Slide 12: Membranes vs Slow Sand?
Approach velocity for membranes is 8 – 50 mm/s
Approach velocity for SSF is 12 cm/hr = 33 mm/s
Both slow sand and membranes form a filter cake on top of the filter.
Both slow sand and membranes can operate without any coagulant
Slow sand particle removal depends on aluminum!
In a slow sand filter it is called ripening
In a membrane filter it is called fouling?

## Slide 13: Example product: MEMCOR XS submerged membrane system
Treated capacity from 7.5 – 25 L/s
Compact footprint: 2.4 m x 4.4 m
Net velocity: 0.7 – 2.4 mm/s
This is the area required for the submerged membranes and thus can be compared to the granular filtration area
Notes: https://www.evoqua.com/en/brands/Memcor/Pages/memcor-xs.aspx

## Slide 14: Floc/floc blanket/sed before membranes?
“If the raw water turbidity and/or NOM concentration is high, pretreatment will include coagulation, flocculation, and sedimentation.”
No indication of what “high” means
Pilot testing recommended
Note that the water industry doesn’t know how to design pilot tests for floc/sed systems that perform as well as full scale
Water and Wastewater Engineering: Design Principles and Practice. Mackenzie Davis

## Slide 15: Membrane fouling
Reduction in flow due to accumulation of particles and adsorbed species
Can be reduced with chemical treatment

## Slide 16: Membrane Story: Temple Texas
  Expect to treat 15 MGD (2004)
  Membranes from Pall Corporation
  No pretreatment
  $14,800,000
Reduced flow after 1st year 11.6 MGD
2008 upgrade
  New chemical clean in place system $590,524
  Flocculation/Sedimentation $2,607,785
  Total cost – $35,263 per L/s of capacity
2017 capacity reduced to 6 mgd
Notes: $14,800,000
https://www.kpaengineers.com/portfolio-items/membrane-filtration-plant/
15 MGD
No pretreatment
$22500 /(L/s)
Actuually operates at 11.6 MGD
Project Description: The City of Temple, Texas owns and operates the 11.6 MGD Membrane Water Treatment Plant. The plant was placed into operation in 2004 and operated as originally designed for the first 12 to 15 months. However, over the past several years the plant has not been able to consistently operate at the design capacity. $590,524 to upgrade the chemical cleaning
Realized they needed pretreatment in 2008
Flocculation/Sedimentation $2,607,785
2017 down to 6 mgd
http://www.tdtnews.com/news/article_679b5530-a629-11e7-8d69-0ff68a1a883c.html
See https://moralescompany.com/completed-projects/water-treatment-plants for lots of photos

## Slide 17
Notes: See https://moralescompany.com/completed-projects/water-treatment-plants for lots of photos

## Slide 18: What’s missing
What solids concentration can membrane filters handle?
How do coagulant nanoparticles interact with membrane filters?
What is the mechanism responsible for head loss build up?
How do membranes handle dissolved organic matter?

## Slide 19: Case 1: load a membrane filter with a clay suspension
What is the head loss as a function of time assuming the clay forms a uniform layer on the membrane?
Raw water turbidity = 5 NTU

## Slide 20: Case 2: pore blocking analysis
Each clay particle blocks one pore
This causes the velocity through the remaining pores to increase and thus the head loss increases

## Slide 21
Number clay particles per unit area
Pores per unit area