## Slide 1: Inlet and Outlet Manifolds and Plant Hydraulics
Using direct fluid feedback rather than indirect computer feedback to control flows
In which Kinetic Energy BECOMES SIGNIFICANT
(Thanks to A.A. Milne)

## Slide 2: Nomenclature: a start
Symbol | Description | Sub | 
Q | Flow | P | Port
A | Area | M | Manifold
H | Piezometric head | D | Diffuser
hL | Total Head Loss |  | 
HGL | Hydraulic Grade Line |  | 
EGL | Energy Grade Line |  | 
Cp | Pressure Coefficient (includes shear and expansion effects) |  | 
Pvc | Area of the vena contracta divided by the orifice area = 0.62 |  | 
D | Diameter |  | 
P | Dimensionless ratio |  | 
n | Number of ports |  | 

## Slide 3: Will the flow be the same?
Dh
Long
Short
Dh = head loss for long route = head loss for short route (if KE is ignored)
Q for long route < Q for short route
K=1
K=1
K=1
K=0.2
K=0.5
K=1
NO!
An example to illustrate the concepts
Notes: 3

## Slide 4: Flow Division Analysis
Short path head loss = long path head loss
expansions
wall shear
Total head loss
Switch velocity to flow
Notes: Head loss is the same for both routes!
The loss coefficient is different and that means that the flows will be different too.

## Slide 5: How did the flow divide?
Long
Short
K=1
K=1
K=1
K=0.2
Improve this?
Set PQ to 0.95

## Slide 6: 4 strategies
Make the paths identical (often not possible)
Add custom head loss to each path (complicated!)
Increase identical head loss in all paths to make differences insignificant
  Orifice head loss in sed effluent manifold
  Diffuser pipes have high exit velocities
Reduce head loss and pressure recovery that cause differences in piezometric head
  Use large diameter pipes for manifolds
Rule of thumb - exit and entrance velocities must be greater than manifold velocity!

## Slide 7: Plant Flow Distribution
Equal flow between sed tank bays?
Equal flow through diffusers into sed tank?
Equal flow between plate settlers?
Equal flow through ports into sludge drain
Where could we add useful head loss? ___________________
After flocs are removed
Notes: We currently use flow restrictions in the effluent launder to divide the flow between the sedimentation tanks.

## Slide 8: Flow distribution
Inlet channel
Settled water outlet channel
Flocculated water to waste
Pipe stubs to block sed tank inlet manifolds
Weir that controls water level in sed tank (and flocculator)
Sensor access to floc hopper
Which sed tank will have the highest flow?
Notes: #6 will have the highest flow rate if inlet channel has a constant cross sectional area.

## Slide 9: Sedimentation tank controls
Entrance from the flocculator
Weir that maintains the water level in the flocculator when flocculating to waste
Wall between inlet and outlet channels
Exit to the filters
Exit weir that maintains the water level in the sedimentation tank (and flocculator)
Drain for flocculated water

## Slide 10: Sed Tank as a Circuit: Flow Distribution Challenge
Inlet channel
Settled water outlet channel
Inlet manifold
Diffuser exit loss
Launder orifice loss
Floc blanket and plate settlers
Effluent manifold (Launder)
Piezometric head change from
Flow deceleration and head loss
Battery creates 5 to 10 cm of potential energy to drive the flow
Piezometric head change from flow acceleration and head loss
Launder exit losses
Flow distribution thru parallel paths is a major hydraulic design challenge
Notes: We will cover this in manifold hydraulics if we have time. Which resistance is good and improves flow distribution? Which resistance makes flow distribution poor?
Improve by increasing losses in diffusers and in orifices

## Slide 11: How can we make water split equally between several paths in a manifold?
Draw a manifold with ports that you think would give unequal flow
Draw a manifold with ports that you think would give equal flow
What do you think is important?
Notes: Vertical manifold or manifold at a slant?
Draw slanted pipe in a lake and discuss what causes water to flow in a pipe

## Slide 12: Flow distribution between ports in a manifold
Which port is going to get the most flow?
There is a very gradual flow expansion!
The water is being stopped by pressure on the end cap
Where is the manifold pressure highest?
n-1
2
n
1
Notes: Draw manifold in lake picture
Define Pi.Q= Qp1/Qpn
Define H average (=vjet^2/2g) and DH (vpipe^2/2g) showing manometers
Note that shape of inlet (pitot tube) matters
DH proportional to 1/A^2 (from orifice eq)
How do you get Pi.Q = 1?
H average > DH
Ajet<Apipe

## Slide 13: Manifold: Flow Calculations
We will derive equations in terms of Hydraulic Grade Line (HGL) because piezometric head controls the port flow
Port flow
  based on _______ equation
Piezometric head change (H) across port
  flow expansion
Piezometric head change (H) between ports
  Darcy-Weisbach and Swamee-Jain
orifice
In manifold

## Slide 14: Inlet Manifold
1
n-1
2
n
EGL
HGL
Major head loss
Pressure recovery
Notes: Which port has the highest flow

## Slide 15: What is total SDHexpansion as a function of n?
Approaches for large n
_______________ is recovered for very gradual expansion.
All kinetic energy

## Slide 16: Outlet Manifold (Launder)
1
n-1
2
n
All of the changes at the ports sum to
Flow contractions, thus no significant minor loss!
EGL
HGL

## Slide 17: Head Loss in a Manifold (same for inlet or outlet)
Define manifold length as
Head loss in a manifold is __ of the head loss with constant Q.
1/3

## Slide 18: Conclusions
Manifolds are complicated (and important)!
Manifold head loss is 1/3 the head loss in a pipe
Difference in piezometric head drives the flow through the ports
Manifold kinetic energy is converted to pressure increase
Following slides develop equations for detailed design of manifolds (reference for your future careers!)

## Slide 19: Change in Piezometric Head in an Outlet Manifold
Note: We have factored out the friction factor knowing that and thus f is not constant
Total change in piezometric head

## Slide 20: Change in Piezometric Head in an Inlet Manifold
This equation gives the difference in piezometric head between the first port and the last port. Since the two terms have opposite signs the maximum difference could be at an intermediate port. We need to determine if one of these terms dominates to see if the maximum difference really is between the first and last ports.

## Slide 21: Calculating the Control (Orifice) Pressure Coefficients
For a manifold the short path head loss is zero (not including the flow control head loss)
0

## Slide 22: Minor Loss Coefficient for an Orifice Port (in or out)
But this V is the vena contracta velocity. The control coefficient analysis normalizes everything to the maximum velocity in the manifold. So let’s get the velocity ratio
Ke has a value of 1 for an exit and is close to 1 for an entrance
Notes: We are changing the scaling velocity used to turn the loss coefficient into a head loss from the vena contracta velocity to the maximum velocity in the manifold. It as if we are pretending that this head loss were occurring in the manifold pipe rather than in the ports exiting or entering the pipe.

## Slide 23: Solution Path
The length of the manifold will be determined by the plant geometry
The spacing of the ports will be set by other constraints
We need to determine the diameter of the manifold and the diameter of the ports

## Slide 24: Launder: Traditional Design Guidelines
Recommended port velocity is 0.46 to 0.76 m/s (Water Treatment Plant Design 4th edition page 7.28)
  The corresponding head loss is 3 to 8 cm through the orifices
  How do you design the diameter of the launder? (coming up…)
  Would this work if head loss through the manifold were an additional 10 cm? _____
NO!
Notes: Water Treatment Plant Design 4th edition page 7.28

## Slide 25: Design Constraints
For sed tank Inlet Manifold the port velocities and the manifold diameter are set by the _____________________________________
For the launder that takes clear water from the top of the sed tank bays the goal will be to keep head loss low and greater than construction errors in level of weir (we aim for about 5 cm)
energy dissipation rate in the flocculator

## Slide 26: Design for Outlet Launder
Given target head loss between sed tank and clear water channel (5 cm for AguaClara)
Solve the minor loss equation for the manifold diameter
Minor loss equation
0

## Slide 27: Outlet Launder Diameter: Iterative solution for DM
The iterative solution will converge quickly because f varies slowly with Re.

## Slide 28: Example Code for Iteration
Error ← 1
While Error > MaxError
MaxError ← _____
First guess at solution
Improved guess
Return y1
Dimensionless error
Set error to be large to ensure that loop executes once

## Slide 29: Launder Diameter (Approximate Solution)
Here we are omitting the major (wall shear) head loss contribution
In this equation the head loss is the total head loss for both the orifices and the pipe flow

## Slide 30: Example: Launder
What is the minimum launder diameter for a plant flow rate of 50 L/s divided between 8 bays if we use 5 cm of head loss? For an approximate solution you can omit the effect of the major losses. Use a value of 0.8 for the minimum flow ratio between the last and first orifice

## Slide 31: Example: Launder
What is the effect of the shear force?
How can we estimate the length of the launder? We will assume that the sed bay has a width of 1 m.
What is the length of the sedimentation tank?
V↑ = 1 mm/s

## Slide 32: Example: Launder
n is the number of orifices (ports). If the port spacing is 10 cm how many are there?
62
For large n
1.36

## Slide 33: More exact solution…
What diameter launder do you recommend?
6 inches

## Slide 34: Why is the launder diameter so large?
(50L/s /9) launder of 6 inches
The head loss in the launder is small and it would be tempting to use a smaller pipe
Why is such a large pipe necessary?______________
Why do we even need a launder pipe? ___________________________________________ ___________
What is the max velocity above the plate settlers given a 1 m wide tank, 25 cm of water above the plates, a single launder? __________
Equal orifice flow
For uniform flow distribution between (and within) plate settlers
2 mm/s
Notes: I take the last question as a real question. Do we actually need launders? Would it be better to lay a perforated cloth on top of the plate settlers to help get uniform flow distribution between plates and then use a simple orifice in the channel wall to create 5 cm of head loss to force flow between bays to be equal?

## Slide 35: What is the horizontal velocity above the plate settlers without a launder?
This velocity is very large compared with the head loss through the plate settlers (about 1 mm) and thus elimination of the launder would result in preferential flow through the plate settlers closest to the exit

## Slide 36: Approach to Find Port Diameter
Calculate the head loss in the manifold
Subtract 50% of that head loss from the target head loss (5 cm) to estimate the port head loss
Calculate the port diameter directly using the orifice equation

## Slide 37: What about Inlet Manifold Design?
Total head loss is not a constraint (it will be VERY small)
Energy dissipation rate at the inlet of the manifold determines the manifold diameter
Energy dissipation rate at the inlet to the diffuser pipes will set the diffuser diameter
Available pipe sizes for inlet manifold and for the diffusers is a constraint

## Slide 38: Schulz and Okun guidelines: Note these cause floc breakup!
VPort = 0.2 to 0.3 m/s (assumes no diffusers)
“The velocity through the ports should be 4x higher than any approaching velocities.” (but to prevent sedimentation approach velocities need to be 0.15 m/s which would give velocities of 0.6 m/s!)
These guidelines result in extremely high energy dissipation rates!

## Slide 39: Schulz and Okun famous quote…
“In practice, one can rarely meet all four basic requirements because they conflict with one another; thus a reasonable compromise must be attained.”
Conclusion of inlet design for sedimentation tanks.
Page 135 in Surface Water Treatment for Communities in Developing Countries
Notes: Page 133 Schulz and Okun quote…
The velocity through the ports should be about 4 times higher than any approaching velocities in order to equalize flow distribution both horizontally and vertically.
To avoid breaking up floc, the velocity gradient through inlet conduits and ports should be held down to a value close to or a little higher than that in the last portion of the flocculator.
The maximum feasible number of ports should be provided in order to minimize the length of the turbulent entry zone produced by the diffusion of the submerged jets from the ports in the perforated baffle inlet
The port configuration should be such as to assure that the discharge jets will direct the flow toward the basin outlet.

## Slide 40: Flow Distribution Equation for Inlet Manifold
Control resistance by orifice
0
What can we play with to get a better flow distribution?
Notes: The pressure recovery term is large relative to the head loss term and the head loss term OVER estimates the role of head loss because the pipe flow isn’t fully developed and the boundary layer is laminar for a significant length of the pipe.
Make manifold area larger than total port area
Increase Kep (make long riser pipes that have significant major or minor losses)

## Slide 41: Area ratio if the DM and DD cause the same eMax
But apparently energy dissipation rate doesn’t matter!
Notes: As we increase the number of ports the diameter of the ports is decreasing. In order to maintain the same energy dissipation rate in the jets issuing from the ports as was in the entrance to the manifold pipe, the velocity in the ports must be LOWER than the velocity in the manifold pipe. Thus the total area of the ports increases slowly as the number of ports increases

## Slide 42: Importance of Area Ratio
Effect of pressure recovery
ports
Notes: Based on full port by port solution

## Slide 43: One more Issue: Vena Contracta with High Velocity Manifold
The vena contracta at each port must be much more pronounced (small Pvc) when the velocity inside the manifold is high.
If the vena contracta, Pvc, is smaller, then the velocities are higher and the energy dissipation rate is higher.
This requires further investigation

## Slide 44: Manifold Conclusions
Outlet manifolds (launder) require an iterative design to get the manifold diameter
Inlet manifold design has complex constraints…
  Avoid breaking flocs
  Don’t let flocs settle (ignore if ports are on bottom)
  Distribute flow uniformly
  Eliminate horizontal velocity in the sed tank
  Produce jets to resuspend flocs to form floc blanket

## Slide 45: Head loss in an AguaClara Plant
Why isn’t there much head loss between the flocculator and the launder pipe?
How do we ensure that the flow divides equally between sedimentation tanks?
10
50
L/s
Rapid Mix Orifice
Rapid Mix Pipe
Flocculator
Launder
Settled water weir
Cumulative head loss (cm)

## Slide 46: Settled Water Weir: Controls the Plant Level
With a maximum H of 5 cm the sedimentation tank water level can change a total of 10 cm! Launders have 5 cm of head loss also.
H is water level measured from the top of the weir
Notes: Our design has changed since this analysis. Now the weir is as wide as a sed tank for the flow of the sed tank

## Slide 47: Hydraulic Conclusions
The water level in the plant is set by the settled water weir
The most significant head loss in the sedimentation tank is the orifices in the launder
The water level increases through the flocculator.
The entrance tank water level is significantly higher than the flocculator due to head loss in the rapid mix orifice
The stock tanks have to be even higher to be able to flow by gravity thru the chemical doser and into the entrance tank.